Supplementary Material

# 1. Case study parameter settings

Table 1

Electric power system node parameters

| Node | Node type | Voltage range / p.u. | Load / kW | Number of users |
| --- | --- | --- | --- | --- |
| Ne1 | Slack | 1 | - | - |
| Ne2 | PQ | [0.9,1.1] | 100 | 37 |
| Ne3 | PQ | [0.9,1.1] | 90 | 52 |
| Ne4 | PQ | [0.9,1.1] | 120 | 18 |
| Ne5 | PQ | [0.9,1.1] | 60 | 44 |
| Ne6 | PV | [0.9,1.1] | 60 | 9 |
| Ne7 | PQ | [0.9,1.1] | 200 | 58 |
| Ne8 | PQ | [0.9,1.1] | 200 | 23 |
| Ne9 | PQ | [0.9,1.1] | 60 | 41 |
| Ne10 | PV | [0.9,1.1] | 60 | 16 |
| Ne11 | PQ | [0.9,1.1] | 60 | 35 |
| Ne12 | PQ | [0.9,1.1] | 0 | 0 |
| Ne13 | PQ | [0.9,1.1] | 60 | 49 |
| Ne14 | PQ | [0.9,1.1] | 120 | 12 |
| Ne15 | PQ | [0.9,1.1] | 60 | 60 |
| Ne16 | PQ | [0.9,1.1] | 60 | 27 |
| Ne17 | PQ | [0.9,1.1] | 60 | 19 |
| Ne18 | PV | [0.9,1.1] | 90 | 8 |
| Ne19 | PQ | [0.9,1.1] | 90 | 33 |
| Ne20 | PQ | [0.9,1.1] | 150 | 14 |
| Ne21 | PQ | [0.9,1.1] | 90 | 46 |
| Ne22 | PQ | [0.9,1.1] | 90 | 25 |
| Ne23 | PQ | [0.9,1.1] | 90 | 54 |
| Ne24 | PQ | [0.9,1.1] | 420 | 11 |
| Ne25 | PV | [0.9,1.1] | 420 | 39 |
| Ne26 | PQ | [0.9,1.1] | 60 | 17 |
| Ne27 | PQ | [0.9,1.1] | 60 | 29 |
| Ne28 | PQ | [0.9,1.1] | 60 | 43 |
| Ne29 | PQ | [0.9,1.1] | 120 | 21 |
| Ne30 | PQ | [0.9,1.1] | 200 | 31 |
| Ne31 | PQ | [0.9,1.1] | 150 | 15 |
| Ne32 | PQ | [0.9,1.1] | 210 | 26 |
| Ne33 | PV | [0.9,1.1] | 60 | 30 |

Note: The voltage is expressed in per-unit (p.u.) values, with a base voltage of 12.66 kV.

Table 2

Electric power system line parameters

| Line | From Node | To Node | Resistance / p.u. | Reactance / p.u. | Length /km | Capacity /MW |
| --- | --- | --- | --- | --- | --- | --- |
| L1-2 | 1 | 2 | 0.09 | 0.05 | 1.4 | 7 |
| L2-3 | 2 | 3 | 0.49 | 0.25 | 0.8 | 7 |
| L3-4 | 3 | 4 | 0.37 | 0.19 | 1.9 | 7 |
| L4-5 | 4 | 5 | 0.38 | 0.19 | 0.3 | 7 |
| L5-6 | 5 | 6 | 0.82 | 0.71 | 1.1 | 7 |
| L6-7 | 6 | 7 | 0.19 | 0.62 | 2.0 | 7 |
| L7-8 | 7 | 8 | 0.71 | 0.24 | 0.6 | 7 |
| L8-9 | 8 | 9 | 1.03 | 0.74 | 1.7 | 7 |
| L9-10 | 9 | 10 | 1.04 | 0.74 | 0.2 | 7 |
| L10-11 | 10 | 11 | 0.20 | 0.07 | 1.5 | 7 |
| L11-12 | 11 | 12 | 0.37 | 0.12 | 0.9 | 7 |
| L12-13 | 12 | 13 | 1.47 | 1.16 | 1.3 | 7 |
| L13-14 | 13 | 14 | 0.54 | 0.71 | 0.4 | 7 |
| L14-15 | 14 | 15 | 0.59 | 0.53 | 1.8 | 7 |
| L15-16 | 15 | 16 | 0.75 | 0.55 | 1.0 | 7 |
| L16-17 | 16 | 17 | 1.29 | 1.72 | 0.7 | 7 |
| L17-18 | 17 | 18 | 0.73 | 0.57 | 1.6 | 7 |
| L2-19 | 2 | 19 | 0.16 | 0.16 | 0.1 | 4 |
| L19-20 | 19 | 20 | 1.50 | 1.36 | 1.2 | 4 |
| L20-21 | 20 | 21 | 0.41 | 0.48 | 0.5 | 4 |
| L21-22 | 21 | 22 | 0.71 | 0.94 | 1.9 | 4 |
| L3-23 | 3 | 23 | 0.45 | 0.31 | 0.8 | 4 |
| L23-24 | 23 | 24 | 0.90 | 0.71 | 1.4 | 4 |
| L24-25 | 24 | 25 | 0.90 | 0.70 | 0.0 | 4 |
| L6-26 | 6 | 26 | 0.20 | 0.10 | 1.7 | 3 |
| L26-27 | 26 | 27 | 0.28 | 0.14 | 0.6 | 3 |
| L27-28 | 27 | 28 | 1.06 | 0.93 | 1.1 | 3 |
| L28-29 | 28 | 29 | 0.80 | 0.70 | 1.5 | 3 |
| L29-30 | 29 | 30 | 0.51 | 0.26 | 0.3 | 3 |
| L30-31 | 30 | 31 | 0.97 | 0.96 | 2.0 | 3 |
| L31-32 | 31 | 32 | 0.31 | 0.36 | 0.9 | 3 |
| L32-33 | 32 | 33 | 0.34 | 0.53 | 1.8 | 3 |
| L8-21 | 8 | 21 | 2.00 | 2.00 | 0.2 | 2 |
| L9-15 | 9 | 15 | 2.00 | 2.00 | 1.3 | 2 |
| L12-22 | 12 | 22 | 2.00 | 2.00 | 0.7 | 2 |
| L18-33 | 18 | 33 | 0.50 | 0.50 | 1.6 | 2 |
| L25-29 | 25 | 29 | 0.50 | 0.50 | 0.4 | 2 |
| LTR2-18 | TR2 | 18 | 0.50 | 0.50 | 1.0 | 1 |
| LGT-18 | GT | 18 | 0.50 | 0.50 | 1.2 | 1 |

Table 3

Natural gas system node parameters

| Node | Node type | Pressure range /MPa | Load/(m³·h⁻¹) | Number of users |
| --- | --- | --- | --- | --- |
| Ng1 | Source | 4 | - | - |
| Ng2 | Load | [3.1,4.2] | 40 | 31 |
| Ng3 | Load | [3.1,4.2] | 80 | 100 |
| Ng4 | Connection | [3.1,4.2] | - | - |
| Ng5 | Source | 3 | - | - |
| Ng6 | Connection | [2.8,4.0] | - | - |
| Ng7 | Load | [3.0,4.0] | 0 | 0 |
| Ng8 | Load | [3.1,4.0] | 80 | 80 |
| Ng9 | Load | [3.1,4.0] | 60 | 37 |

Table 4

Natural gas system line parameters

| Pipeline | From Node | To Node | Diameter /m | Length /km | Capacity /(m³·h⁻¹) |
| --- | --- | --- | --- | --- | --- |
| G1-2 | Ng1 | Ng2 | 0.88 | 7 | 400 |
| G2-3 | Ng2 | Ng3 | 0.88 | 12 | 400 |
| G3-4 | Ng3 | Ng4 | 0.88 | 10 | 400 |
| G2-6 | Ng2 | Ng6 | 0.88 | 10 | 400 |
| G5-6 | Ng5 | Ng6 | 0.88 | 7 | 400 |
| G6-7 | Ng6 | Ng7 | 0.88 | 12 | 400 |
| G7-8 | Ng7 | Ng8 | 0.88 | 10 | 400 |
| G4-8 | Ng4 | Ng8 | 0.88 | 7 | 400 |
| G4-9 | Ng4 | Ng9 | 0.88 | 7 | 400 |
| G8-9 | Ng8 | Ng9 | 0.88 | 10 | 400 |

Compressors CP1 and CP2 both adopt the fixed pressure-ratio control mode [1], and their detailed parameters are listed in Table 5.

Table 5

Compressor parameters

|  | B | Z | H | Failure rate (occ./yr) | Repair time (h) |
| --- | --- | --- | --- | --- | --- |
| CP1 | 228.7 | 0.233 | 1.20 | 0.03 | 50 |
| CP2 | 226.0 | 0.233 | 1.05 | 0.03 | 50 |

Following [2], the electricity load nodes are divided into three levels according to importance, and the importance coefficients ε are listed in Table 6. The importance coefficients of the natural gas load nodes are [ω2 ω3 ω8 ω9] = [0.8 0.6 1.0 0.6].

Table 6

Importance coefficients of EPS load nodes

| Level | Node | ε |
| --- | --- | --- |
| Level I | Ne7, Ne14, Ne18, Ne24, Ne25 | 1.0 |
| Level II | Ne2, Ne8, Ne12, Ne15, Ne19, Ne22, Ne28, Ne32 | 0.5 |
| Level III | Ne3, Ne4, Ne5, Ne6, Ne9, Ne10, Ne11, Ne13, Ne16, Ne17, Ne20, Ne21, Ne23, Ne26, Ne27, Ne29, Ne30, Ne33 | 0.1 |

The daily load factor curve in [3] is adopted to characterize the intraday load level at each node, as shown in Fig. 1.

Fig. 1 Daily load factor curve

To characterize seasonal load variations and differences between weekdays and weekends, this paper adopts the load adjustment coefficient in [4], as listed in Table 7. The base loads of each load node are given in Table 1 and Table 3. Loads at different times are characterized by multiplying the base load by the daily load factor and load adjustment coefficient.

Table 7

Load adjustment coefficients

|  | Weekly factor |  | Seasonal factor |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | Weekday | Weekend | Spring | Summer | Autumn | Winter |
| Electric load | 1 | 0.8 | 0.7 | 1.0 | 0.8 | 0.9 |
| Gas load | 1 | 0.8 | 0.7 | 1.0 | 0.9 | 1.0 |

The energy purchase prices of electricity and gas are shown in Fig. 2. To reduce operating costs, the lower-cost energy-supply mode is preferentially selected by jointly considering energy prices and coupling unit efficiencies.

Fig. 2 Energy purchase prices

- Q. Zeng, J. Fang, et al. Steady-state analysis of the integrated natural gas and electric power system with bi-directional energy conversion. Applied Energy 2016; 184: 1483-1492.

- S. Zhang, W. Liu, et al. Reliability assessment of regional integrated energy systems considering multiple thermal inertia characteristics. Transactions of China Electrotechnical Society 2023; 38(12): 3289-3305. (in Chinese)

- N. Yan, Z. Zhao, et al. Multi-time scales low-carbon economic dispatch of integrated energy system considering hydrogen and electricity complementary energy storage. Journal of Energy Storage 2024; 104: 114514.

- A. Shahmohammadi, M. Moradi-Dalvand, et al. Optimal design of multicarrier energy systems considering reliability constraints. IEEE Trans. Power Delivery 2015; 30(2): 878-886.

# 2. Capacity coupling degree of different schemes

Table 8

Capacity coupling degree of different schemes

| Scenario | Scheme | CU,P2G (MW) | CU,GT (MW) | (%) | (%) | (%) |
| --- | --- | --- | --- | --- | --- | --- |
| No Coupling | 0 | 0 | 0 | 0 | 0 | 0 |
| Gas-to-Electricity | 1-1 | 0 | 0.11 | 0 | 0.63 | 0.63 |
|  | 1-2 | 0 | 0.22 | 0 | 1.26 | 1.26 |
|  | 1-3 | 0 | 0.33 | 0 | 1.89 | 1.89 |
|  | 1-4 | 0 | 0.44 | 0 | 2.52 | 2.52 |
|  | 1-5 | 0 | 0.55 | 0 | 3.15 | 3.15 |
|  | 1-6 | 0 | 0.66 | 0 | 3.78 | 3.78 |
|  | 1-7 | 0 | 0.77 | 0 | 4.41 | 4.41 |
|  | 1-8 | 0 | 0.88 | 0 | 5.04 | 5.04 |
|  | 1-9 | 0 | 0.99 | 0 | 5.67 | 5.67 |
|  | 1-10 | 0 | 1.1 | 0 | 6.3 | 6.30 |
| Electricity-to-Gas | 2-1 | 0.17 | 0 | 0.85 | 0 | 0.85 |
|  | 2-2 | 0.34 | 0 | 1.7 | 0 | 1.70 |
|  | 2-3 | 0.51 | 0 | 2.55 | 0 | 2.55 |
|  | 2-4 | 0.68 | 0 | 3.4 | 0 | 3.40 |
|  | 2-5 | 0.85 | 0 | 4.25 | 0 | 4.25 |
|  | 2-6 | 1.02 | 0 | 5.1 | 0 | 5.10 |
|  | 2-7 | 1.19 | 0 | 5.95 | 0 | 5.95 |
|  | 2-8 | 1.36 | 0 | 6.8 | 0 | 6.80 |
|  | 2-9 | 1.53 | 0 | 7.65 | 0 | 7.65 |
|  | 2-10 | 1.7 | 0 | 8.5 | 0 | 8.50 |
| Bidirectional coupling | 3-1 | 0.17 | 0.11 | 0.85 | 0.63 | 1.48 |
|  | 3-2 | 0.34 | 0.22 | 1.7 | 1.26 | 2.96 |
|  | 3-3 | 0.51 | 0.33 | 2.55 | 1.89 | 4.44 |
|  | 3-4 | 0.68 | 0.44 | 3.4 | 2.52 | 5.92 |
|  | 3-5 | 0.85 | 0.55 | 4.25 | 3.15 | 7.40 |
|  | 3-6 | 1.02 | 0.66 | 5.1 | 3.78 | 8.88 |
|  | 3-7 | 1.19 | 0.77 | 5.95 | 4.41 | 10.36 |
|  | 3-8 | 1.36 | 0.88 | 6.8 | 5.04 | 11.84 |
|  | 3-9 | 1.53 | 0.99 | 7.65 | 5.67 | 13.32 |
|  | 3-10 | 1.7 | 1.1 | 8.5 | 6.3 | 14.80 |

# 3. Reliability assessment for IES

## 3.1 Optimal load shedding model

Following an IES contingency, energy balance must be maintained through measures such as the redispatch of energy supply units and load shedding. An optimal load shedding model determines the optimal unit outputs and load shedding scheme subject to all IES operational constraints, such that a predefined objective is optimized [5]. The model proposed in [6] is adopted in this paper.

### 3.1.1 Objective function

The objective is to minimize the economic cost of shedding loads with different priority levels in the IES.

(1)

where, Nt is the number of samples; NE and NG are the numbers of EPS and NGS nodes, respectively;  and  are the active power curtailed at electricity node i and the load curtailed at gas node m at time t, respectively; CE and CG are the unit load shedding costs of electricity and natural gas, respectively; εi and ωm are the importance coefficients of electricity node i and gas node m, respectively [7].

Under this objective, loads with higher shedding costs are preferentially maintained. Consequently, low-cost loads in one subsystem may be shed to supply high-cost loads in another subsystem through coupling units.

Note that although the input node of a coupling unit is modeled as a load node, its load-shedding amount is not included in the objective function [5], because the corresponding supply loss has already been accounted for at the output side of the coupling unit.

### 3.1.2 Constraints

The constraints in [6] are adopted in this paper and are detailed as follows.

1) EPS

(2)

Eq. (2-1) and (2-2) are the AC power flow equations and node balance equations, respectively. Pi,t and Qi,t are the active and reactive power injected at node i at time t, respectively; Ui,t denotes the voltage of node i at time t; Gij and Bij are the conductance and susceptance of line ij; θij,t is the voltage phase angle difference between the two ends of line ij at time t;  is the reactive power curtailed at node i at time t;  and  are the active and reactive power outputs of generator g at time t;  is the active power output of gas-fired generator (GT) m at time t;  and  are the active and reactive loads of node i at time t; , , , and  are the set of nodes, generators, GTs, and lines connected to node i, respectively.

Eq. (2-3) and (2-4) are the load shedding constraints and nodal voltage constraints, respectively. Ui,min and Ui,max are the minimum and maximum voltages of node i, respectively.

Eq. (2-5) and (2-6) are the generator capacity and line capacity constraints, respectively.  and  are the state parameters of generator g and line b at time t, which are equal to 1 when the component is normal and 0 when it has failed;  and  are the maximum active and reactive power outputs of generator g;  is the apparent power of line b at time t; .. is the capacity of line b.

2) NGS

(3)

Eq. (3-1) is the pipeline flow equation [8].  is the gas flow in pipeline p at time t; πi,t and πj,t are the pressures of nodes i and j at time t, respectively; signp(πi,t,πj,t) is the sign function indicating the flow direction, which is +1 when πi,t≥πj,t and -1 otherwise; Kp is the pipeline constant; T0 is the standard temperature; dp is the diameter of pipeline p;  is the natural gas density; p0 is the standard atmospheric pressure; TG is the natural gas temperature; Z is the compressibility factor; Gl,p is the length of pipeline p; p is the gas-specific heat ratio.

Eq. (3-2) is the gas-turbine-driven compressor model [8].  is the flow consumed by the compressor on pipeline p at time t; Bp and Zp are compressor parameters; Hp is the compressor pressure ratio.

Eq. (3-3) and (3-4) are the nodal flow balance equation and loop nodal pressure balance equation, respectively [8].  is the gas supply flow of gas well w at time t;  is the gas supply flow of P2G unit n at time t; ,  and  are the set of gas wells, P2G units and pipelines connected to node i, respectively; is the load flow at node i at time t; Gc is a loop in the NGS;  is the pressure drop of pipeline p at time t.

Eq. (3-5) and (3-6) are the load shedding constraints and nodal pressure constraints, respectively. πi,min and πi,max are the minimum and maximum pressures of node i, respectively.

Eq. (3-7) and (3-8) are the pipeline flow capacity constraint and gas well capacity constraint, respectively.  and  are the capacities of pipeline p and gas well w, respectively.

3) Coupling unit

As the gas-to-electricity coupling unit, a GT is modeled as follows [5]:

(4)

Eq. (6-1) and (6-2) are the GT power balance equation and capacity constraint, respectively.  is the natural gas flow input to GT m at time t;  is the efficiency of GT m;  is the input capacity of GT m.

As the electricity-to-gas coupling unit, P2G is modeled as follows [5]:

(5)

Eq. (7-1) and (7-2) are the P2G power balance equation and capacity constraint, respectively.  is the active power input of P2G n at time t;  is the efficiency of P2G n;  is the input capacity of P2G n.

## 3.2 Reliability indices

To evaluate the reliability of the IES, this paper adopts the average energy availability index (AEAI) as the reliability index [7]. It is calculated as follows:

(6)

where, SAIDI is the system average interruption duration index [7]; Ny is the number of simulated years; Nt is the number of samples in one year; Ncum,IES is the total number of users in IES; Nl is the number of load nodes; Ncum,i is the number of users of node i;  is the outage duration of node i in year y (h).

## 3.3 Transmission delay and inertia of natural gas

For the natural gas system (NGS), when a failure occurs, there is a non-negligible time delay for natural gas to travel from the gas source to the load point (transmission delay), while the nodal gas pressure can remain within an acceptable range for a certain period (inertia) [6]. Therefore, following the method in [6], the effects of transmission delay and inertia are taken into account when calculating the number and duration of supply interruptions in the NGS.

Considering the transmission delay of gas flow in the NGS, the actual supply restoration time tre of a natural gas load node is calculated as follows:

(7)

where, tr is the component repair time; Gl,z is the length of path z between the load and the gas source; vz is the natural gas flow velocity along path z; and  is the set of paths between the load and the gas source.

The transient model of pressure and flow at a natural gas load node [6] is given by

(8)

where, x and t are the spatial and temporal variables, respectively; S and μ are the pipeline cross-sectional area and pipeline friction factor, respectively; v is the natural gas flow velocity; RM is the molar mass of natural gas; and g is the gravitational acceleration.

Eq. (8) is a second-order dynamic equation and is computationally complicated to solve directly. Therefore, it is first transformed into the Laplace domain. By substituting the minimum allowable nodal pressure pmin, the time tp for the pressure at the load node to decrease to pmin is obtained.

(9)

Similarly, after tre is obtained, the actual minimum pressure pf at the load node is calculated based on Eq. (9). Following the same procedure, pf is then substituted into the equation to obtain the time th required for the pressure to recover from pf to pmin.

In summary, during IES reliability assessment, when the gas supply is interrupted, the actual supply interruption state and outage duration should be calculated according to Eq. (10), considering both the gas inertia at the load node and the transmission delay of gas flow.

(10)

where, Ry is the actual supply interruption state of the load, with Ry=0 indicating a supply interruption and Ry=1 indicating no supply interruption; and  is the actual duration for which the gas supply does not satisfy the required level.

## 3.4 Reliability assessment procedure

The sequential Monte Carlo simulation method in [6] is adopted to evaluate the reliability of the IES. The method performs reliability assessment using time-series data covering one year with a time step of 1 h. The assessment procedure is shown in Fig. 3 and consists of the following steps:

1) Input the parameters of the IES and its components, and initialize the block counter (d=1) and the number of simulated years (y=1).

2) Generate 1000-year state-duration sequences for all components.

3) Select a 24-h block and solve the system optimal load shedding model for the block under the simulated component states.

4) Account for the inertia and transmission delay of natural gas, and correct the number and duration of system supply interruptions.

5) If the simulated samples reach one year (d=365), set y=y+1; otherwise, set d=d+1 and return to Step 3).

6) If the number of simulated years reaches the upper limit (y>1000), proceed to Step 7); otherwise, set d=1 and return to Step 3).

7) Calculate the AEAI according to Eq. (6).

Fig. 3 Flowchart of the IES reliability assessment procedure

- Z. Zeng, T. Ding, et al. Reliability evaluation for integrated power-gas systems with power-to-gas and gas storages. IEEE Trans. Power Systems 2020; 35(1): 571-583.

- M. Jiang, B. Wang, G. Li. A reliability evaluation method for integrated energy system with hydrogen considering gas inertia and delay of flow. IEEE Conference on Energy Internet and Energy System Integration (EI2) 2024, p. 1368-1374.

- Y. Lei, K. Hou, et al. A new reliability assessment approach for integrated energy systems: Using hierarchical decoupling optimization framework and impact-increment based state enumeration method. Applied Energy 2018; 210: 1237-1250.

- J. Xiao, C. Wang, et al. Quantitative analysis of multi-energy coupling: Indicator set and influence on IES region. Applied Energy 2025; 401: 126619.

# 4. Detailed analysis of unidirectional coupling

## 4.1 Condition 2: flow from LCS to HRS

In the case study, NGS is the LCS. The EPS adopts a dual-source closed-loop structure and is therefore considered an HRS, with AEAIE=99.9680%.

Unidirectional rule 2: When energy flows from the LCS to an HRS, the reliability of the inflow subsystem, outflow subsystem, and IES remains almost unchanged initially. When coupling changes the energy supply path during normal operation of the inflow subsystem, reliability changes. If the path deteriorates, the reliability of all three systems decreases. If the path improves, the reliability of the inflow subsystem slightly increases, while the reliability of the outflow subsystem decreases, resulting in either a decrease or a slight increase in IES reliability. Afterward, the reliability of all systems remains unchanged.

The following sections analyze the variation rules and mechanisms of the outflow subsystem, inflow subsystem, and IES reliability with coupling degree.

1) Outflow subsystem

Under G2E coupling, the relationship between NGS reliability and coupling degree is shown in Fig. 4.

Fig. 4 NGS reliability versus coupling degree under G2E coupling

As shown in Fig. 4, with increasing coupling degree, NGS reliability decreases slightly at first. When the coupling degree reaches 3.14%, the reliability decreases significantly and then remains unchanged.

Unidirectional rule 2-1: When energy flows from the LCS to an HRS, the reliability of the outflow subsystem decreases slightly at first. When coupling changes the energy supply path during normal operation of the inflow subsystem, the reliability of the outflow subsystem decreases. Afterward, the reliability remains unchanged.

Mechanism: For an HRS, the demand for cross-system support is very low, and thus the impact on the outflow subsystem is limited, resulting in only a slight initial decrease in reliability. When coupling changes the energy supply path during normal operation of the inflow subsystem, part of the load is supplied by the outflow subsystem. Since the outflow subsystem is the LCS, it preferentially supplies the inflow subsystem after failures, resulting in insufficient self-supply capability and reduced reliability. After this point, increasing the coupling degree no longer changes the energy supply path. The external energy supply from the outflow subsystem no longer increases, and its reliability remains unchanged.

In this case, when the coupling degree reaches 3.14%, Ne19–Ne22 changes from grid supply to GT supply. The external energy supply from NGS increases by 0.42 MW. Since the natural gas load shedding cost (0.6 EUR/kWh) is lower than the electricity load shedding cost (11.0 EUR/kWh), after NGS failures, priority is given to supplying Ne19–Ne22, which increases the supply interruption of NGS. For example, when NG1 fails, the interrupted load increases from 0 to 0.12 MW.

2) Inflow subsystem

Under G2E coupling, the relationship between EPS reliability and coupling degree is shown in Fig. 5.

Fig. 5 EPS reliability versus coupling degree under G2E coupling

As shown in Fig. 5, EPS reliability initially increases slightly with increasing coupling degree. When the coupling degree reaches 3.14%, reliability decreases and then remains unchanged.

Unidirectional rule 2-2: When energy flows from the LCS to an HRS, the reliability of the inflow subsystem first increases slightly. When coupling changes the energy supply path during normal operation, the reliability decreases if the path deteriorates, while it increases slightly if path improves. Afterward, reliability remains unchanged.

Mechanism: An HRS already has sufficient redundancy of energy supply paths. Therefore, the reliability improvement brought by coupling is insignificant, resulting in only a slight initial increase. When the coupling degree becomes sufficiently large, the energy supply path during normal operation changes due to differences in energy purchase costs. If the new path deteriorates, reliability decreases. If the new path improves, reliability increases only slightly because the original reliability level is already high. Afterward, further increasing the coupling degree no longer changes the energy supply path, and the reliability remains unchanged.

In this case, when the coupling degree reaches 3.14%, the GT capacity becomes sufficient to independently supply Ne19–Ne22. Meanwhile, because GT supply has a lower cost, Ne19–Ne22 switches to GT supply. The supply path length increases from 1.5 km to 19 km, indicating deterioration of the supply path, which leads to reduced reliability.

3) IES

Under G2E coupling, the relationship between IES reliability and coupling degree is shown in Fig. 6.

Fig. 6 IES reliability versus coupling degree under G2E coupling

As shown in Fig. 6, with increasing coupling degree, IES reliability remains unchanged initially. When the coupling degree reaches 3.14%, reliability decreases and then remains unchanged.

Unidirectional rule 2-3: When energy flows from the LCS to an HRS, IES reliability remains almost unchanged initially. When coupling changes the energy supply path during normal operation of the inflow subsystem, IES reliability changes: it decreases if the path deteriorates and may decrease or slightly increase if the path improves. Afterward, reliability remains unchanged.

Mechanism: After coupling, IES reliability is the combination of subsystem reliabilities. According to rules 2-1 and 2-2, IES reliability initially remains almost unchanged. When coupling deteriorates the energy supply path during normal operation of the inflow subsystem, the reliability of both subsystems decreases, leading to reduced IES reliability. When the path improves, the reliability of the inflow subsystem slightly increases, while the reliability of the outflow subsystem decreases. If the improvement impact exceeds the deterioration impact, IES reliability slightly increases; otherwise, it decreases. Afterward, the reliability of both subsystems remains unchanged, and therefore the IES reliability also remains unchanged.

## 4.2 Condition 3: flow from LCS to LRS

In Conditions 3 and 4, the unit load shedding costs of electricity and natural gas are exchanged, which are set to 0.6 EUR/kWh and 11.0 EUR/kWh, respectively.

After exchanging the unit load shedding costs, EPS becomes the LCS. NGS remains an LRS, AEAIG= 99.9143%.

Unidirectional rule 3: When energy flows from the LCS to an LRS, the reliability of the inflow subsystem and the IES increases with increasing coupling degree, while the reliability of the outflow subsystem decreases. Finally, the reliability of all three systems reaches saturation.

The following sections analyze the variation rules and mechanisms of the outflow subsystem, inflow subsystem, and IES reliability with coupling degree.

1) Outflow subsystem

After exchanging load shedding costs, under E2G unidirectional coupling, the relationship between EPS reliability and coupling degree is shown in Fig. 7.

Fig. 7 EPS reliability versus coupling degree under E2G coupling (after exchanging load shedding costs)

As shown in Fig. 7, EPS reliability decreases initially and then reaches saturation with increasing coupling degree.

Unidirectional rule 3-1: When energy flows from the LCS to an LRS, the reliability of the outflow subsystem decreases with increasing coupling degree and finally reaches saturation.

Mechanism: After failures, the LCS preferentially provides external energy supply. Since an LRS has a high demand for cross-system support, the outflow subsystem may suffer insufficient self-supply capability, resulting in reduced reliability. With increasing coupling degree, the amount of external energy supply increases, leading to further reliability deterioration. When the supply interruption of the inflow subsystem is eliminated or the external supply capability of the outflow subsystem is restricted by line capacity, the external energy supply no longer increases, and the reliability reduction reaches saturation.

In this case, when the coupling degree reaches 6.80%, the supply interruption caused by failure of G2-3 is eliminated. Therefore, the external energy supply from EPS no longer increases, the reliability reduction reaches saturation.

2) Inflow subsystem

After exchanging load shedding costs, under E2G coupling, the relationship between NGS reliability and coupling degree is shown in Fig. 8.

Fig. 8 NGS reliability versus coupling degree under E2G coupling (after exchanging load shedding costs)

As shown in Fig. 8, NGS reliability increases first and then reaches saturation with increasing coupling degree.

Unidirectional rule 3-2: When energy flows from the LCS to an LRS, the reliability of the inflow subsystem increases with increasing coupling degree and finally reaches saturation.

Mechanism: For an LRS, coupling introduces additional energy supply paths, reducing supply interruption after failures and improving reliability. With increasing coupling degree, the supply capability of the additional path increases, resulting in fewer supply interruptions. When the supply interruption of the inflow subsystem is eliminated or the external supply capability is restricted by line capacity, the reliability no longer increases.

3) IES

After exchanging load shedding costs, under E2G unidirectional coupling, the relationship between IES reliability and coupling degree is shown in Fig. 9.

Fig. 9 IES reliability versus coupling degree under E2G coupling (after exchanging load shedding costs)

As shown in Fig. 9, IES reliability increases first and then reaches saturation with increasing coupling degree.

Unidirectional rule 3-3: When energy flows from the LCS to an LRS, IES reliability increases with increasing coupling degree and finally reaches saturation.

Mechanism: LRS has a large amount of supply interruption that can be eliminated through coupling. Moreover, only when the LCS fails does it need to shed its own loads to provide external energy supply, while it operates normally during most periods. Therefore, the reduction in supply interruption of the LRS is more than the additional interruption caused by external energy supply from the LCS, resulting in improved IES reliability. With increasing coupling degree, more supply interruptions are eliminated, and IES reliability increases. When the supply interruption of the LRS is eliminated or the external energy supply capability of the LCS is restricted by line capacity, the improvement in IES reliability reaches saturation.

## 4.3 Condition 4: flow from HCS to HRS

After exchanging the unit load shedding costs, NGS becomes the HCS, while EPS remains the HRS.

Unidirectional rule 4: When energy flows from the HCS to an HRS, the reliability of the inflow subsystem and IES first increases slightly. When coupling changes the energy supply path during normal operation of the inflow subsystem, the reliability decreases if the path deteriorates, while it increases only slightly if the path improves. Afterward, the reliability of both systems remains unchanged. The reliability of the outflow subsystem remains unchanged throughout.

The following sections analyze the variation rules and mechanisms of the outflow subsystem, inflow subsystem, and IES reliability with coupling degree.

1) Outflow subsystem

After exchanging unit load shedding costs, under G2E coupling, the relationship between NGS reliability and coupling degree is shown in Fig. 10.

Fig. 10 NGS reliability versus coupling degree under G2E coupling (after exchanging load shedding costs)

As shown in Fig. 10, NGS reliability remains unchanged with increasing coupling degree.

Unidirectional rule 4-1: When energy flows from the HCS to an HRS, the reliability of the outflow subsystem remains unchanged.

Mechanism: For the HCS, self-supply is preferentially maintained. Therefore, after failures, it does not shed its own loads to support the inflow subsystem, and its reliability remains unchanged after coupling.

2) Inflow subsystem

After exchanging unit load shedding costs, under G2E coupling, the relationship between EPS reliability and coupling degree is shown in Fig. 11.

Fig. 11 EPS reliability versus coupling degree under G2E coupling (after exchanging load shedding costs)

As shown in Fig. 11, EPS reliability first increases slightly with increasing coupling degree. When the coupling degree reaches 3.14%, reliability decreases and then remains unchanged.

Unidirectional rule 4-2: When energy flows from the HCS to an HRS, the reliability of the inflow subsystem first increases slightly. When coupling changes the supply path during normal operation, the reliability decreases if the path deteriorates and increases only slightly if the path improves. Afterward, reliability remains unchanged.

Mechanism: An HRS already has sufficient redundancy of energy supply paths. Therefore, the reliability improvement caused by coupling is insignificant, resulting in only a slight initial increase. When the coupling degree becomes sufficiently large, the energy supply path during normal operation changes due to differences in energy purchase costs. If the path deteriorates, reliability decreases. If the path improves, reliability increases slightly because the original reliability level is already high. Afterward, further increasing the coupling degree no longer changes the supply path, and reliability remains unchanged.

3) IES

After exchanging load shedding costs, under G2E coupling, the relationship between IES reliability and coupling degree is shown in Fig. 12.

Fig. 12 IES reliability versus coupling degree under G2E coupling (after exchanging load shedding costs)

As shown in Fig. 12, IES reliability first increases slightly with increasing coupling degree. When the coupling degree reaches 3.14%, reliability decreases and then remains unchanged.

Unidirectional rule 4-3: When energy flows from the HCS to an HRS, IES reliability first increases slightly. When coupling changes the energy supply path during normal operation of the inflow subsystem, reliability decreases if the path deteriorates and increases only slightly if the path improves. Afterward, reliability remains unchanged.

Mechanism: IES reliability is the combination of subsystem reliabilities. Since the reliability of the outflow subsystem remains unchanged, the variation trend of IES reliability is consistent with that of the inflow subsystem.

# 5. Detailed analysis of bidirectional coupling

## 4.1 Condition 1: HCLRS coupled with LCLRS

The EPS tie line is removed, forming an open-loop structure. EPS becomes an HCLRS and NGS is an LCLRS.

Bidirectional rule 1: When an HCLRS is bidirectionally coupled with an LCLRS, the reliability of both subsystems and the IES increases with increasing coupling degree and finally reaches saturation.

The following sections provide detailed analysis.

1) Subsystem 1: HCLRS

After the tie line is removed, the relationship between EPS reliability and coupling degree under bidirectional coupling is shown in Fig. 13.

Fig. 13 EPS reliability versus coupling degree under bidirectional coupling (tie line removed)

As shown in Fig. 13, EPS reliability increases first and then reaches saturation with increasing coupling degree.

Bidirectional rule 1-1: When an HCLRS is bidirectionally coupled with an LCLRS, the reliability of the HCLRS increases with increasing coupling degree and finally reaches saturation.

Mechanism: HCLRS has insufficient redundancy of energy supply paths. Coupling reduces supply interruptions, and since this system does not shed its own loads to provide external energy supply, its reliability increases. With increasing coupling degree, more supply interruptions are eliminated, leading to higher reliability. When its supply interruptions are eliminated or external energy support is restricted by line capacity, reliability no longer increases.

2) Subsystem 2: LCLRS

After the tie line is removed, the relationship between NGS reliability and coupling degree under bidirectional coupling is shown in Fig. 14.

Fig. 14 NGS reliability versus coupling degree under bidirectional coupling (tie line removed)

As shown in Fig. 14, NGS reliability increases first and then reaches saturation with increasing coupling degree.

Bidirectional rule 1-2: When an HCLRS is bidirectionally coupled with an LCLRS, the reliability of the LCLRS increases with increasing coupling degree and finally reaches saturation.

Mechanism: An LCLRS has a large amount of supply interruption that can be eliminated through coupling. Moreover, it only needs to shed its own loads to provide external energy supply when the high-cost system fails, while the high-cost system operates normally during most periods. Therefore, the reduction in supply interruption of the LCLRS is greater than the additional interruption caused by external energy supply. Its reliability therefore increases. With increasing coupling degree, more supply interruptions are eliminated. When supply interruptions are nearly eliminated or external energy support is restricted by line capacity, reliability no longer increases.

3) IES

After the tie line is removed, the relationship between IES reliability and coupling degree under bidirectional coupling is shown in Fig. 15.

Fig. 15 IES reliability versus coupling degree under bidirectional coupling (tie line removed)

As shown in Fig. 15, IES reliability increases first and then reaches saturation with increasing coupling degree.

Bidirectional rule 1-3: When an HCLRS is bidirectionally coupled with an LCLRS, IES reliability increases with increasing coupling degree and finally reaches saturation.

Mechanism: After coupling, IES reliability is the combination of subsystem reliabilities. Since the reliability of both subsystems increases with coupling degree and finally reaches saturation, the IES reliability follows the same trend.

## 4.2 Condition 2: HCHRS coupled with LCHRS

In the original case study, the NGS is an LCLRS. Therefore, a new pipeline G3–7, with the same parameters as G2–6, is added, as shown in Fig. 16.

Fig. 16 NGS topology after adding G3–7

As shown in Fig. 16, the NGS has a dual-source closed-loop structure. Following a G2–3 failure, G3–7 can supply gas to Ng3, making the NGS a high-reliability system.

Bidirectional rule 2: If an HCHRS is bidirectionally coupled with an LCHRS, the reliabilities of both subsystems and the IES initially remain almost unchanged. When coupling changes the energy supply path during normal operation of subsystem 1, all three reliabilities decrease if the path deteriorates. If the path improves, the reliability of subsystem 2 decreases slightly, whereas those of subsystem 1 and the IES increase slightly. Thereafter, all reliabilities remain unchanged.

The following sections provide detailed analysis.

1) Subsystem 1: HCHRS

After G3–7 is added, the relationship between EPS reliability and coupling degree under bidirectional coupling is shown in Fig. 17.

Fig. 17 EPS reliability versus coupling degree under bidirectional coupling after adding G3–7

As shown in Fig. 17, EPS reliability initially increases slightly. When the coupling degree reaches 8.87%, the reliability increases further and then remains unchanged.

Bidirectional rule 2-1: If an HCHRS is bidirectionally coupled with an LCHRS, the reliability of the HCHRS initially increases slightly. When coupling changes its energy supply path under normal operation, reliability decreases if the path deteriorates and increases slightly if the path improves. Thereafter, reliability remains unchanged.

Mechanism: An HCHRS does not shed its own loads to export energy, and the reliability improvement brought by coupling is limited. Therefore, its reliability initially increases only slightly. When the coupling degree becomes sufficiently large, differences in energy purchase costs may change its energy supply path during normal operation. If the new path deteriorates, reliability decreases. If the path improves, reliability increases only slightly because the original reliability is already high. Thereafter, coupling no longer changes the energy supply path, and reliability remains unchanged.

2) Subsystem 2: LCHRS

After G3–7 is added, the relationship between NGS reliability and coupling degree under bidirectional coupling is shown in Fig. 18.

Fig. 18 NGS reliability versus coupling degree under bidirectional coupling after adding G3–7

As shown in Fig. 18, NGS reliability initially remains unchanged. When the coupling degree reaches 8.87%, it decreases and then remains unchanged.

Bidirectional rule 2-2: If an HCHRS is bidirectionally coupled with an LCHRS, the reliability of subsystem 2 initially remains almost unchanged. When coupling changes the energy supply path during normal operation of subsystem 1, the reliability of subsystem 2 decreases slightly. Thereafter, it remains unchanged.

Mechanism: When two high-reliability systems are coupled, the need for cross-system support is very low, so the reliability degradation caused by coupling is insignificant and the reliability of subsystem 2 initially remains almost unchanged. When coupling changes the energy supply path during normal operation of subsystem 1, subsystem 2 exports more energy and its reliability decreases. However, because subsystem 2 has sufficient supply path redundancy, the decrease is very small. Thereafter, coupling no longer changes the energy supply path, the exported energy no longer increases, and reliability remains unchanged.

3) IES

After G3–7 is added, the relationship between IES reliability and coupling degree under bidirectional coupling is shown in Fig. 19.

Fig. 19 IES reliability versus coupling degree under bidirectional coupling after adding G3–7

As shown in Fig. 19, IES reliability initially increases slightly. When the coupling degree reaches 8.87%, it increases further and then remains unchanged.

Bidirectional rule 2-3: If an HCHRS is bidirectionally coupled with an LCHRS, IES reliability initially remains almost unchanged. When coupling changes the energy supply path during normal operation of subsystem 1, IES reliability changes: it decreases if the path deteriorates and increases slightly if the path improves. Thereafter, reliability remains unchanged.

Mechanism: IES reliability reflects the combined effects of the subsystem reliabilities and therefore initially increases slightly. When coupling deteriorates the energy supply path during normal operation of subsystem 1, the reliabilities of both subsystems decrease and hence IES reliability decreases. If the path improves, the reliability of subsystem 1 increases slightly. Because subsystem 2 is a high-reliability system, additional supply interruption caused by energy export occurs only under a small number of contingency states, and its reliability decreases only slightly. Therefore, the improvement in subsystem 1 dominates, and IES reliability increases slightly. Thereafter, both subsystem reliabilities remain unchanged, and IES reliability also remains unchanged.

## 4.3 Condition 3: HCHRS coupled with LCLRS

For Condition 3, the original parameters of the case study are retained. The EPS is an HCHRS and the NGS is an LCLRS.

Bidirectional rule 3: If an HCHRS is bidirectionally coupled with an LCLRS, the reliabilities of subsystem 1 and the IES initially increase. When coupling changes the energy supply path during normal operation of subsystem 1, both reliabilities decrease if the path deteriorates and increase slightly if the path improves. Thereafter, the reliability of subsystem 1 remains unchanged, whereas IES reliability continues to increase until reaching saturation. The reliability of subsystem 2 continuously increases with coupling degree and eventually reaches saturation.

The following sections provide detailed analysis.

1) Subsystem 1: HCHRS

Under bidirectional coupling, the relationship between EPS reliability and coupling degree is shown in Fig. 20.

Fig. 20 EPS reliability versus coupling degree under bidirectional coupling

As shown in Fig. 20, EPS reliability initially increases slightly. When the coupling degree reaches 8.87%, reliability decreases and then remains unchanged.

Bidirectional rule 3-1: If an HCHRS is bidirectionally coupled with an LCLRS, the reliability of the HCHRS initially increases slightly. When coupling changes its energy supply path during normal operation, reliability decreases if the path deteriorates and increases slightly if the path improves. Thereafter, reliability remains unchanged.

Mechanism: An HCHRS does not shed its own loads to export energy, and the reliability improvement brought by coupling is limited. Therefore, its reliability initially increases slightly. When the coupling degree becomes sufficiently large, differences in energy purchase costs may change its energy supply path during normal operation. If the path deteriorates, reliability decreases. If the path improves, reliability increases only slightly because the original reliability is already high. Thereafter, coupling no longer changes the energy supply path, and reliability remains unchanged.

2) Subsystem 2: LCLRS

Under bidirectional coupling, the relationship between NGS reliability and coupling degree is shown in Fig. 21.

Fig. 21 NGS reliability versus coupling degree under bidirectional coupling

As shown in Fig. 21, NGS reliability first increases with coupling degree and then reaches saturation.

Bidirectional rule 3-2: If an HCHRS is bidirectionally coupled with an LCLRS, the LCLRS reliability increases with coupling degree and eventually reaches saturation.

Mechanism: Coupling can eliminate a relatively large amount of supply interruption in subsystem 2, while subsystem 1 has a very low demand for cross-system support. Therefore, the reduction in supply interruption in subsystem 2 exceeds the additional supply interruption caused by energy export, and its reliability increases with coupling degree. Once its supply interruption is eliminated, or the external energy it can receive is limited by branch capacity, reliability no longer increases.

3) IES

Under bidirectional coupling, the relationship between IES reliability and coupling degree is shown in Fig. 22.

Fig. 22 IES reliability versus coupling degree under bidirectional coupling

As shown in Fig. 22, IES reliability first increases. When the coupling degree reaches 7.40%, reliability decreases and then continues to increase until reaching saturation.

Bidirectional rule 3-3: If an HCHRS is bidirectionally coupled with an LCLRS, IES reliability initially increases. When coupling changes the energy supply path during normal operation of subsystem 1, IES reliability decreases if the path deteriorates and increases slightly if the path improves. Thereafter, reliability continues to increase and eventually reaches saturation.

Mechanism: IES reliability reflects the combined effects of the subsystem reliabilities. Since the reliabilities of both subsystems initially increase, IES reliability also increases. When coupling changes the energy supply path during normal operation of subsystem 1, IES reliability decreases if the path deteriorates and increases slightly if the path improves. Thereafter, the reliability of subsystem 1 remains unchanged, while IES reliability continues to increase with the reliability of subsystem 2. Once the supply interruption in subsystem 2 is eliminated, or the external energy it can receive is limited by branch capacity, IES reliability no longer increases.

## 4.4 Condition 4: HCLRS coupled with LCHRS

For Condition 4, the load shedding costs of the two subsystems are interchanged. The NGS becomes an HCLRS, whereas the EPS becomes an LCHRS.

Bidirectional rule 4: If an HCLRS is bidirectionally coupled with an LCHRS, the reliability of subsystem 1 increases with coupling degree and eventually reaches saturation. The reliability of subsystem 2 initially decreases, whereas IES reliability initially increases. When coupling changes the energy supply path during normal operation of subsystem 2, both reliabilities decrease if the path deteriorates and increase slightly if the path improves. Thereafter, the reliability of subsystem 2 continues to decrease, whereas IES reliability continues to increase, and both eventually reach saturation.

The following sections provide detailed analysis.

1) Subsystem 1: HCLRS

After the cost swap, the relationship between NGS reliability and coupling degree under bidirectional coupling is shown in Fig. 23.

Fig. 23 NGS reliability versus coupling degree under bidirectional coupling after the cost swap

As shown in Fig. 23, NGS reliability first increases with coupling degree and then reaches saturation.

Bidirectional rule 4-1: If an HCLRS is bidirectionally coupled with an LCHRS, the HCLRS reliability increases with coupling degree and eventually reaches saturation.

Mechanism: An HCLRS has insufficient supply path redundancy. Coupling eliminates part of its supply interruption, and because it does not shed its own loads to export energy, its reliability increases. As the coupling degree increases, more supply interruption is eliminated and reliability increases. Once its supply interruption is eliminated, or the external energy it can receive is limited by branch capacity, reliability no longer increases.

2) Subsystem 2: LCHRS

After the cost swap, the relationship between EPS reliability and coupling degree under bidirectional coupling is shown in Fig. 24.

Fig. 24 EPS reliability versus coupling degree under bidirectional coupling after the cost swap

As shown in Fig. 24, EPS reliability initially decreases slowly. When the coupling degree reaches 8.87%, reliability decreases significantly and then continues to decrease slowly until reaching saturation.

Bidirectional rule 4-2: If an HCLRS is bidirectionally coupled with an LCHRS, the reliability of the LCHRS initially decreases. When coupling changes its energy supply path during normal operation, reliability decreases if the path deteriorates and increases slightly if the path improves. Thereafter, reliability continues to decrease and eventually reaches saturation.

Mechanism: Coupling can eliminate only a small amount of supply interruption in subsystem 2, whereas subsystem 1 has a high demand for cross-system support. Therefore, the reduction in supply interruption in subsystem 2 is smaller than the additional supply interruption caused by energy export, and its reliability decreases. When the coupling degree becomes sufficiently large, differences in energy purchase costs may change the energy supply path during normal operation of subsystem 2. If the path deteriorates, reliability decreases. If the path improves, reliability increases only slightly because its original reliability is already high. Thereafter, the supply interruption continues to increase and reliability decreases further. Once the supply interruption in subsystem 1 is eliminated, or the external energy is limited by branch capacity, subsystem 2 reliability no longer decreases.

3) IES

After the cost swap, the relationship between IES reliability and coupling degree under bidirectional coupling is shown in Fig. 25.

Fig. 25 IES reliability versus coupling degree under bidirectional coupling after the cost swap

As shown in Fig. 25, IES reliability first increases. When the coupling degree reaches 7.40%, reliability decreases and then continues to increase until reaching saturation.

Bidirectional rule 4-3: If an HCLRS is bidirectionally coupled with an LCHRS, IES reliability initially increases. When coupling changes the energy supply path during normal operation of subsystem 2, IES reliability decreases if the path deteriorates and increases slightly if the path improves. Thereafter, IES reliability continues to increase and eventually reaches saturation.

Mechanism: Subsystem 1 has low reliability, so coupling can eliminate a relatively large amount of supply interruption. Subsystem 2 has sufficient supply path redundancy, and the additional supply interruption caused by energy export is relatively small. Therefore, the supply interruption eliminated by coupling exceeds the additional supply interruption, and IES reliability increases. When coupling changes the energy supply path during normal operation of subsystem 2, IES reliability decreases if the path deteriorates and increases slightly if the path improves. Thereafter, the supply interruption continues to decrease and IES reliability increases. Once the supply interruption in subsystem 1 is eliminated, or the external energy it can receive is limited by branch capacity, IES reliability no longer increases.

# 6. Validation on an 81-Node IES

## 6.1 Case overview

A large-scale electricity–gas coupled test system is constructed using the IEEE 69-node distribution system [9] and the 12-node natural gas system in Ref. [10], as shown in Fig. 26.

Fig. 26 Topology of the 81-node system

The distribution system operates in an open-loop mode, with tie lines put into operation only for network reconfiguration following contingencies. The natural gas system operates in an open-loop mode before coupling and switches to a closed-loop mode after the P2G unit is connected.

The branch and node parameters of the electricity and natural gas systems are taken from Refs. [9] and [10], respectively. The component reliability parameters, load adjustment coefficients, and other parameters are the same as those of the base case in Section 4.

## 6.2 Rule validation

For each of the three coupling scenarios, ten different coupling degrees are considered, as listed in Table 9.

Table 9

Capacity coupling degrees of selected schemes

| Scenario | Scheme | CU,P2G (MW) | CU,GT (MW) | (%) | (%) | (%) |
| --- | --- | --- | --- | --- | --- | --- |
| Uncoupled | 0 | 0 | 0 | 0 | 0 | 0 |
| G2E | 1-1 | 0 | 0.4 | 0 | 1.6 | 1.6 |
|  | … |  |  |  |  |  |
|  | 1-10 | 0 | 4.0 | 0 | 16.0 | 16.0 |
| E2G | 2-1 | 0.3 | 0 | 1.05 | 0 | 1.05 |
|  | … |  |  |  |  |  |
|  | 2-10 | 3.0 | 0 | 10.50 | 0 | 10.50 |
| Bidirectional | 3-1 | 0.3 | 0.4 | 1.05 | 1.6 | 2.65 |
|  | … |  |  |  |  |  |
|  | 3-10 | 3.0 | 4.0 | 10.50 | 16.0 | 26.50 |

### 6.2.1 Validation of unidirectional coupling rules

(1) Unidirectional rule 1

The unit load-shedding costs of electricity and natural gas are interchanged and set to 0.6 EUR/kWh and 11.0 EUR/kWh, respectively. Therefore, the EPS becomes a low-cost system, whereas the NGS becomes a high-cost system.

Fig. 27 System reliability versus coupling degree under G2E coupling (after exchanging load shedding costs)

In this test system, the EPS has a single-source closed-loop structure and is therefore a low-reliability system, whereas the NGS has a dual-source closed-loop structure and is therefore a high-reliability system.

Under G2E coupling, energy flows from the high-cost system to low-reliability system. The relationship between system reliability and coupling degree is shown in Fig. 27.

As shown in Fig. 27, with increasing coupling degree:

1) The reliability of the high-cost system, i.e., the NGS, remains unchanged, validating Unidirectional rule 1-1.

2) The reliability of the low-reliability system, i.e., the EPS, first increases and then reaches saturation, validating Unidirectional rule 1-2.

3) IES reliability first increases and then reaches saturation, validating Unidirectional rule 1-3.

(2) Unidirectional rule 2

After the load-shedding costs are interchanged, E2G coupling corresponds to energy flowing from the low-cost system to the high-reliability system. The relationship between system reliability and coupling degree is shown in Fig. 28.

Fig. 28 System reliability versus coupling degree under E2G coupling (after exchanging load shedding costs)

As shown in Fig. 28, with increasing coupling degree:

1) The reliability of the low-cost system, i.e., the EPS, decreases slightly, validating Unidirectional rule 2-1.

2) The reliability of the high-reliability system, i.e., the NGS, increases slightly, validating Unidirectional rule 2-2.

3) IES reliability increases slightly, validating Unidirectional rule 2-3.

(3) Unidirectional rule 3

Under the original parameter settings of the test system, G2E coupling corresponds to energy flowing from the low-cost system to the low-reliability system. The relationship between system reliability and coupling degree is shown in Fig. 29.

Fig. 29 System reliability versus coupling degree under G2E coupling

As shown in Fig. 29, with increasing coupling degree:

1) The reliability of the low-cost system, i.e., the NGS, first decreases and then reaches saturation, validating Unidirectional rule 3-1.

2) The reliability of the low-reliability system, i.e., the EPS, first increases and then reaches saturation, validating Unidirectional rule 3-2.

3) IES reliability first increases and then reaches saturation, validating Unidirectional rule 3-3.

(4) Unidirectional rule 4

Under the original parameter settings of the test system, E2G coupling corresponds to energy flowing from the high-cost system to the high-reliability system. The relationship between system reliability and coupling degree is shown in Fig. 30.

Fig. 30 System reliability versus coupling degree under E2G coupling

As shown in Fig. 30, with increasing coupling degree:

1) The reliability of the high-cost system, i.e., the EPS, remains unchanged, validating Unidirectional rule 4-1.

2) The reliability of the high-reliability system, i.e., the NGS, increases slightly, validating Unidirectional rule 4-2.

3) IES reliability increases slightly, validating Unidirectional rule 4-3.

### 6.2.2 Validation of bidirectional coupling rules

(1) Bidirectional rule 1

In the original test system, the NGS is a low-cost high-reliability system. Therefore, pipeline G3-8 is removed, as shown in Fig. 31.

Fig. 31 NGS topology after removing G3-8

As shown in Fig. E6, failure of G2-3 causes a supply interruption at Ng3, while failure of G7-8 causes a supply interruption at Ng8. Therefore, G2-3 and G7-8 are weak components, and the NGS becomes a low-reliability system.

The EPS is a high-cost low-reliability system, whereas the NGS is a low-cost low-reliability system.

After G3-8 is removed, the reliability of the system is calculated for different schemes, as shown in Fig. 32.

Fig. 32 System reliability versus coupling degree under bidirectional coupling (after removing G3-8)

As shown in Fig. 32, with increasing coupling degree:

1) The reliability of the high-cost low-reliability system, i.e., the EPS, first increases and then reaches saturation, validating Bidirectional rule 1-1.

2) The reliability of the low-cost low-reliability system, i.e., the NGS, first increases and then reaches saturation, validating Bidirectional rule 1-2.

3) IES reliability first increases and then reaches saturation, validating Bidirectional rule 1-3.

(2) Bidirectional rule 2

In the test system, the EPS is a high-cost low-reliability system. Therefore, transformer TR2, with the same parameters as the original transformer, is added, as shown in Fig. 33.

Fig. 33 EPS topology after adding TR2

As shown in Fig. E8, after TR2 is added, the EPS forms a dual-source closed-loop structure and becomes a high-reliability system.

The EPS is therefore a high-cost high-reliability system, whereas the NGS is a low-cost high-reliability system.

After TR2 is added, the reliability of the system is calculated for different schemes, as shown in Fig. 34.

Fig. 34 System reliability versus coupling degree under bidirectional coupling (after adding TR2)

As shown in Fig. 34:

1) When the coupling degree reaches 2.65%, coupling changes the normal-operation energy supply path of the high-cost high-reliability EPS, and the path improves. Consequently, EPS reliability increases slightly and then remains unchanged, validating Bidirectional rule 2-1.

2) When the coupling degree reaches 2.65%, coupling changes the normal-operation energy supply path of the EPS. The reliability of the low-cost high-reliability NGS decreases and then increases slightly, validating Bidirectional rule 2-2.

3) When the coupling degree reaches 2.65%, coupling changes the normal-operation energy supply path of the EPS, and the path improves. Consequently, IES reliability increases and then increases slightly thereafter, validating Bidirectional rule 2-3.

(3) Bidirectional rule 3

After the load-shedding costs are interchanged, the EPS becomes a low-cost low-reliability system, whereas the NGS becomes a high-cost high-reliability system. The reliability of the system is calculated for different schemes, as shown in Fig. 35.

Fig. 35 System reliability versus coupling degree under bidirectional coupling (after exchanging load shedding costs)

As shown in Fig. 35, with increasing coupling degree:

1) The reliability of the high-cost high-reliability system, i.e., the NGS, increases slightly, validating Bidirectional rule 3-1.

2) The reliability of the low-cost low-reliability system, i.e., the EPS, first increases and then reaches saturation, validating Bidirectional rule 3-2.

3) IES reliability first increases and then reaches saturation, validating Bidirectional rule 3-3.

(4) Bidirectional rule 4

Under the original parameter settings of the test system, the EPS is a high-cost low-reliability system, whereas the NGS is a low-cost high-reliability system. The reliability of the system is calculated for different schemes, as shown in Fig. 36.

Fig. 36 System reliability versus coupling degree under bidirectional coupling

As shown in Fig. 36, with increasing coupling degree:

1) The reliability of the high-cost low-reliability system, i.e., the EPS, first increases and then reaches saturation, validating Bidirectional rule 4-1.

2) The reliability of the low-cost high-reliability system, i.e., the NGS, first decreases and then reaches saturation, validating Bidirectional rule 4-2.

3) IES reliability first increases and then reaches saturation, validating Bidirectional rule 4-3.

### 6.2.3 Validation of common rules

(1) Common rule 1

As shown in Figs. 27–30, 32, and 34–E36, the reliability of all low-reliability systems increases after coupling, whereas that of high-reliability systems either decreases or increases slightly. These results validate Common rule 1.

(2) Common rule 2

As shown in Figs. 27–30, 32, and 34–E36, the reliability of high-cost systems either increases or remains unchanged, whereas that of low-cost systems tends to decrease. These results validate Common rule 2.

(3) Common rule 3

As shown in Figs. 27–30, the reliability of all inflow subsystems increases, whereas that of the outflow subsystems either decreases or remains unchanged. These results validate Common rule 3.

(4) Common rule 4

As shown in Fig. 34, EPS reliability increases after its normal-operation energy supply path improves, validating Common rule 4.

- W. Liu, Y. Wang, et al. Multi-stage restoration strategy to enhance distribution system resilience with improved conditional generative adversarial nets. CSEE Journal of Power and Energy Systems 2025; 11(4): 1657-1669.

- B. Fan, et al. Economic-emission-constrained multi-objective hybrid optimal energy flow of integrated energy systems. International Journal of Low-Carbon Technologies 2023; 18: 265-272.

# 7. Calculation procedure for the planning method in existing study

## 7.1 Planning model

To ensure the comparability of the planning results, the original network topology and independent energy-supply units of the IES are fixed, and only the capacities of the GT and P2G units are treated as planning variables. Expansion of other facilities, such as electric lines, natural gas pipelines, gas storage, and demand response resources, is not considered. The connection locations, efficiencies, failure rates, and repair times of the GT and P2G units are the same as this paper.

Ref. [11] minimizes the total system cost:

(11)

where, Ctotal is the annual total cost of the IES; Cinv, Cop, and Closs are the annualized investment cost of the coupling units, annual system operating cost, and annual supply interruption cost, respectively.

The investment cost of the coupling units is expressed as

(12)

where,  and  are the annualized unit investment costs of the GT and P2G units, respectively; and  and  are the input capacities of the GT and P2G units, respectively.

The system operating cost mainly includes the costs of purchasing electricity from the superior power grid and natural gas from the natural gas stations:

(13)

where,  and  are the electricity and natural gas purchase prices at time t, respectively; and  and  are the amounts of purchased electricity and natural gas at time t, respectively.

The supply interruption cost is calculated as

(14)

where,  and  are the load shedding amounts at electricity node i and natural gas node m, respectively; and  and  are the unit load shedding costs of electricity and natural gas, respectively.

The remaining constraints, including the electric power flow, natural gas flow, and nodal voltage constraints, are the same as those in the model described in Section 3.1.2.

Ref. [11] adopts system average interruption frequency index (SAIFI) as the reliability constraint. To maintain consistency with the average energy availability index (AEAI) adopted in this paper, the reliability constraint is replaced by

(15)

## 7.2 Planning results

The planning model in Section 7.1 is solved using the method in Ref. [11]. The planning results obtained without and with the recommendations proposed in this paper are compared in Table 10.

Table 10

Comparison of results under different planning schemes

| Planning scheme | Coupling unit capacity | Total cost (104 CNY/year) | Investment cost (104 CNY/year) | Operating cost (104 CNY/year) | Supply interruption cost (104 CNY/year) | AEAIE (%) | AEAIG (%) | AEAIIES (%) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Before planning | CU,GT=0MW, CU,P2G=0MW | 2119.60 | 0.00 | 2063.71 | 55.89 | 99.9680 | 99.9143 | 99.9596 |
| Scheme of [11] | CU,GT=0.55MW, CU,P2G=0MW | 2115.22 | 17.51 | 2037.27 | 60.44 | 99.9614 | 99.9050 | 99.9495 |
| Change | - | −4.38 | +17.51 | −26.44 | +4.55 | −0.0066 | −0.0093 | −0.0101 |
| Scheme of this paper | CU,GT=0MW, CU,P2G=1.14MW | 2118.98. | 15.35 | 2064.36 | 39.27 | 99.9680 | 99.9845 | 99.9705 |
| Change | - | -0.62 | +15.35 | +0.65 | -16.62 | 0 | +0.0702 | +0.0109 |

As shown in Table D1, the planning scheme obtained using the method in Ref. [15] adopts G2E coupling, with a GT capacity of 0.55 MW. After planning, the total IES cost decreases by 4.37×104 CNY/year, while the reliability indices AEAIE, AEAIG, and AEAIIES decrease by 0.0066%, 0.0093%, and 0.0101%, respectively.

If the system owner seeks to avoid reliability degradation, the reliability thresholds are increased to AEAIE≥99.9680%, AEAIG≥99.9143%, and AEAIIES≥99.9596%. According to the recommendations proposed in this paper, E2G coupling is adopted, and the resulting P2G capacity is 1.14 MW. After planning, the total IES cost decreases by 0.62×104 CNY/year. Meanwhile, AEAIG and AEAIIES increase by 0.0702% and 0.0109%, respectively, while AEAIE remains unchanged.

- C. He, Y. Zhou, et al. Reliability-constrained distributionally robust expansion planning of integrated electricity-gas distribution system with demand response. Energy 2025; 321: 135409.